## AutoCAD
DB-HD1 |  |  | SDB1
Pi, kW | 5.802 | [15 empty] | BOARDER
К | 0.53192
Pd, kW | 3.0862 | [15 empty] | OF RANGE
соs f | 0.97821
Ib, A | 4.7934
Isc(3), kA | 5.3812 |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
[5 empty] | 0 | DIFF_2pole+KM | DIFF_2pole+KM | DIFF_2pole | DIFF_2pole | DIFF_2pole | DIFF_2pole | DIFF_2pole | DIFF_2pole | DIFF_2pole | DIFF_2pole | CB_1pole | CB_1pole
Да | Pd, kW | Ib, A | PMF, % |  | 1 | QFD1 | QFD2 | QFD3 | QFD4 | QFD5 | QFD6 | QFD7 | QFD8 | QFD9 | QFD10 | QF11 | QF12
L1 | 1.672 | 7.8033 | 27.8559 |  | 2 | iDPN N Vigi | iDPN N Vigi | iDPN N Vigi | iDPN N Vigi | iDPN N Vigi | iDPN N Vigi | iDPN N Vigi | iDPN N Vigi | iDPN N Vigi | iDPN N Vigi | iC60N | iC60N
L2 | 1.798 | 8.3395 | 22.8988 |  | 3 | AC C10A | AC C10A | AC C10A | AC C10A | AC C10A | AC C10A | AC C10A | AC C10A | AC C10A | AC C10A | C16A | C16A
L3 | 2.332 | 10.8163 | 0 |  | 4 | 30мА | 30мА | 30мА | 30мА | 30мА | 30мА | 30мА | 30мА | 30мА | 30мА
5
L1 | 1.672 | 7.8033 |  |  | 1: 6
L2 | 1.798 | 8.3395 |  |  | 1: 7
L3 | 2.332 | 10.8163 |  |  | 1: 8; QFD1: KM1; QFD2: KM2
L1,L2,L3 | 0 | 0 |  |  | 1: 9; QFD1: iCT; QFD2: iCT
[5 empty] | 10 | 16А | 16А
[5 empty] | 11 | 220В | 220В
Income breaker | Add. Device | SDB breaker |  |  | 1: Income cable
QS |  | QF |  |  | 1: ППГнг(А)-HF 5x4
iSW |  | NSX100N | bar: 1; QF12
C40A |  | 100 |  |  | 1: 15
|  | TM100D |  |  | 16 | L1 | L1 | L3 | L2 | L3 | L3 | L2 | L1 | L3 | L2
|  |  |  | 17 | Line name | N1 | N2 | N3 | N4 | N5 | N6 | N7 | N8 | N9 | N10 | N11 | N12
|  |  |  | 18 | Pi, kW | 0.068 | 1.008 | 0.544 | 0.606 | 0.596 | 0.596 | 0.596 | 0.596 | 0.596 | 0.596
|  |  |  | 19 | Pd, kW | 0.068 | 1.008 | 0.544 | 0.606 | 0.596 | 0.596 | 0.596 | 0.596 | 0.596 | 0.596
|  |  |  | 20 | соs f | 0.85 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | 21 | Ib, A | 0.36364 | 4.6753 | 2.5232 | 2.8108 | 2.7644 | 2.7644 | 2.7644 | 2.7644 | 2.7644 | 2.7644
|  |  |  | 22 | Cable mark | ППГнг(А)-HF | ППГнг(А)-HF | ППГнг(А)-HF | ППГнг(А)-HF | ППГнг(А)-HF | ППГнг(А)-HF | ППГнг(А)-HF | ППГнг(А)-HF | ППГнг(А)-HF | ППГнг(А)-HF
|  |  |  | 23 | Cable type | 3x2,5 | 3x2,5 | 3x2,5 | 3x2,5 | 3x2,5 | 3x2,5 | 3x2,5 | 3x2,5 | 3x2,5 | 3x2,5
|  |  |  | 24 | Length, m | 20 | 30 | 60 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
|  |  |  | 25 | Method of installation | Cable tray | Cable tray | Cable tray | Cable tray | Cable tray | Cable tray | Cable tray | Cable tray | Cable tray | Cable tray
|  |  |  | 26 | Voltage drop, % | 0.039797 | 1.0275 | 1.0299 | 0.088249 | 0.086792 | 0.086792 | 0.086792 | 0.086792 | 0.086792 | 0.086792
|  |  |  | 27 | Short current L-N, Isc(1), kA | 0.60702 | 0.38316 | 0.2205 | 1.4586 | 1.4586 | 1.4586 | 1.4586 | 1.4586 | 1.4586 | 1.4586
|  |  |  | 28 | Load name | Convector | Convector | Convector | Convector | Convector | Convector | Convector | Convector | Convector | Convector | Spare | Spare
|  |  |  | 29 | Room number
|  |  |  | 30 |  | ЩР | Розетка | Розетка | Светильник круглый | Розетка | Розетка | Розетка | Розетка | Розетка | Розетка | Нет | Нет
[6 empty] | DB | Socket | Socket | Circle lighting | Socket | Socket | Socket | Socket | Socket | Socket | None | None
DO NOT
[6 empty] | N12: DELETE | 1
COLUMN

## Расчет
1 | 3 | 11 |  |  | Installed power, kW | К summer | К winter | Voltage, V | Pd, kW | Qd., kVAr | Sd., kVA | cos f | Id., A | Pd, kW | Qd., kVAr | Sd., kVA | cos f | Id., A |  | Need table of PMF?
|  |  |  | TOTAL | 5.802 | 0.53192 | 0.53192 | 380 | 3.0862 | 0.65501 | 3.1549 | 0.97821 | 4.7934 | 3.0862 | 0.65501 | 3.1549 | 0.97821 | 4.7934 |  | Да
|  |  | Щиты | 0 | 0 | #DIV/0! | #DIV/0! | 380 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0 | 0 | 0 | #DIV/0! | #DIV/0!
|  |  | Load type 1 | 1 | 0.068 | 1 | 1 | 380 | 0.068 | 0.042143 | 0.08 | 0.85 | 0.12155 | 0.068 | 0.042143 | 0.08 | 0.85 | 0.12155
|  |  | Load type 2 | 2 | 1.008 | 0.9 | 0.9 | 380 | 0.9072 | 0.18421 | 0.92571 | 0.98 | 1.4065 | 0.9072 | 0.18421 | 0.92571 | 0.98 | 1.4065
|  |  | Load type 3 | 3 | 0.544 | 0.8 | 0.8 | 380 | 0.4352 | 0.088371 | 0.44408 | 0.98 | 0.67471 | 0.4352 | 0.088371 | 0.44408 | 0.98 | 0.67471
|  |  | Load type 4 | 4 | 0.606 | 0.7 | 0.7 | 380 | 0.4242 | 0.086137 | 0.43286 | 0.98 | 0.65766 | 0.4242 | 0.086137 | 0.43286 | 0.98 | 0.65766
|  |  | Load type 5 | 5 | 0.596 | 0.6 | 0.6 | 380 | 0.3576 | 0.072614 | 0.3649 | 0.98 | 0.55441 | 0.3576 | 0.072614 | 0.3649 | 0.98 | 0.55441
|  |  | Load type 6 | 6 | 0.596 | 0.5 | 0.5 | 380 | 0.298 | 0.060511 | 0.30408 | 0.98 | 0.462 | 0.298 | 0.060511 | 0.30408 | 0.98 | 0.462
|  |  | Load type 7 | 7 | 0.596 | 0.4 | 0.4 | 380 | 0.2384 | 0.048409 | 0.24327 | 0.98 | 0.3696 | 0.2384 | 0.048409 | 0.24327 | 0.98 | 0.3696
|  |  | Load type 8 | 8 | 0.596 | 0.3 | 0.3 | 380 | 0.1788 | 0.036307 | 0.18245 | 0.98 | 0.2772 | 0.1788 | 0.036307 | 0.18245 | 0.98 | 0.2772
|  |  | Load type 9 | 9 | 0.596 | 0.2 | 0.2 | 380 | 0.1192 | 0.024205 | 0.12163 | 0.98 | 0.1848 | 0.1192 | 0.024205 | 0.12163 | 0.98 | 0.1848
|  |  | Load type 10 | 10 | 0.596 | 0.1 | 0.1 | 380 | 0.0596 | 0.012102 | 0.060816 | 0.98 | 0.092401 | 0.0596 | 0.012102 | 0.060816 | 0.98 | 0.092401
[8 empty] | PANEL TOTAL | [5 empty] | Incomer breaker |  |  | Incomer Type: |  |  | SWITCH_3pole |  | SDB breaker |  |  |  | Income cable | [5 empty] | Additional income device
|  | SDB1 | DB-HD1 | BLOCK |  |  |  | Pi, kW | K | Pр., кВт | cos f | Id., A | Iкз(3) | Type | Name | In, A | Max of CB | Curve | "+line" | Current x 1,25 |  | Scheme designation | Type | In, A | "+line" | Cable mark | Wires | Wire section, mm2 | Length, m |  | dU, % | line 1 | line 2 | line 3 | line 4
[8 empty] | 5.802 | 0.53192 | 3.0862 | 0.97821 | 4.7934 | 5.3812 | QS | iSW | 40 | 16 | C |  | 5.9918 |  | QF | NSX100N | 100 | TM100D | ППГнг(А)-HF | 5 | 4 | 5 |  | 0.027221 | [14 empty] | f2 | f10 | f4 | f6 | f11
|  |  | Placement |  | Load | [8 empty] | Circuit breaker | [7 empty] | Control device |  |  |  | Cable | [11 empty] | MCB breaker config
NN | Feeding from | Line number | Load name | Room number | Installed power, kW | Load type (1 - 10) | cos f | Voltage, V | Pi, kW | Qd., kVAr | Sd., kVA | Id., A | Phase | Type | Name | In, A | dI, mA | Curve | Iрх% | Iddx% | Electromagnet breaker, 25% < Isc(1) | Scheme designation | Type | In, A | Control voltage, V | Cable mark | Wires | Wire section, mm2 | Length for calc, m | Length for specification, m | dU, % | Isc(1), кA | R | X | r1w | x1w | Method of installation | In, A | Breaker current, А | Ток уставки защиты, А | Ток уставки мгновенной отсечки, А | Breaker type | Breaker type | Load legend |  | OPTIMA | ACQUA | ALS.PRS | OWP/R | DAMIN L | ЯТП
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 28 | 7 | 32 | 32 | 30 | 250
[15 empty] | min value | 10 |  | multiplier | 1 | 0.7 | 1.25 | [5 empty] | min value | 2.5 |  | limit | 3
N
1 | DB-HD1 | N1 | Convector |  | 0.068 | 1 | 0.85 | 220 | 0.068 | 0.042143 | 0.08 | 0.36364 | L1 | QFD | iDPN N Vigi | 10 | 30 | AC C | 0.36364 | 17.5 | 0.0625 | KM | iCT | 16 | 220 | ППГнг(А)-HF | 3 | 2.5 | 20 | 20 | 0.039797 | 0.60702 | 7.41 | 0.116 | 148.2 | 2.32 | Cable tray | [5 empty] | DIFF_2pole+KM | ЩР | DB |  |  | 6
2 | DB-HD1 | N2 | Convector |  | 1.008 | 2 | 0.98 | 220 | 1.008 | 0.20468 | 1.0286 | 4.6753 | L1 | QFD | iDPN N Vigi | 10 | 30 | AC C | 4.6753 | 17.5 | 0.0625 | KM | iCT | 16 | 220 | ППГнг(А)-HF | 3 | 2.5 | 30 | 35 | 1.0275 | 0.38316 | 7.41 | 0.116 | 259.35 | 4.06 | Cable tray | [5 empty] | DIFF_2pole+KM | Розетка | Socket |  |  | 6
3 | DB-HD1 | N3 | Convector |  | 0.544 | 3 | 0.98 | 220 | 0.544 | 0.11046 | 0.5551 | 2.5232 | L3 | QFD | iDPN N Vigi | 10 | 30 | AC C | 2.5232 | 17.5 | 0.0625 |  |  |  |  | ППГнг(А)-HF | 3 | 2.5 | 60 | 65 | 1.0299 | 0.2205 | 7.41 | 0.116 | 481.65 | 7.54 | Cable tray | [5 empty] | DIFF_2pole | Розетка | Socket |  |  | 6
4 | DB-HD1 | N4 | Convector |  | 0.606 | 4 | 0.98 | 220 | 0.606 | 0.12305 | 0.61837 | 2.8108 | L2 | QFD | iDPN N Vigi | 10 | 30 | AC C | 2.8108 | 17.5 | 0.0625 |  |  |  |  | ППГнг(А)-HF | 3 | 2.5 | 5 | 5 | 0.088249 | 1.4586 | 7.41 | 0.116 | 37.05 | 0.58 | Cable tray | [5 empty] | DIFF_2pole | Светильник круглый | Circle lighting |  |  | 6
5 | DB-HD1 | N5 | Convector |  | 0.596 | 5 | 0.98 | 220 | 0.596 | 0.12102 | 0.60816 | 2.7644 | L3 | QFD | iDPN N Vigi | 10 | 30 | AC C | 2.7644 | 17.5 | 0.0625 |  |  |  |  | ППГнг(А)-HF | 3 | 2.5 | 5 | 5 | 0.086792 | 1.4586 | 7.41 | 0.116 | 37.05 | 0.58 | Cable tray | [5 empty] | DIFF_2pole | Розетка | Socket |  |  | 6
6 | DB-HD1 | N6 | Convector |  | 0.596 | 6 | 0.98 | 220 | 0.596 | 0.12102 | 0.60816 | 2.7644 | L3 | QFD | iDPN N Vigi | 10 | 30 | AC C | 2.7644 | 17.5 | 0.0625 |  |  |  |  | ППГнг(А)-HF | 3 | 2.5 | 5 | 5 | 0.086792 | 1.4586 | 7.41 | 0.116 | 37.05 | 0.58 | Cable tray | [5 empty] | DIFF_2pole | Розетка | Socket |  |  | 6
7 | DB-HD1 | N7 | Convector |  | 0.596 | 7 | 0.98 | 220 | 0.596 | 0.12102 | 0.60816 | 2.7644 | L2 | QFD | iDPN N Vigi | 10 | 30 | AC C | 2.7644 | 17.5 | 0.0625 |  |  |  |  | ППГнг(А)-HF | 3 | 2.5 | 5 | 5 | 0.086792 | 1.4586 | 7.41 | 0.116 | 37.05 | 0.58 | Cable tray | [5 empty] | DIFF_2pole | Розетка | Socket |  |  | 6
8 | DB-HD1 | N8 | Convector |  | 0.596 | 8 | 0.98 | 220 | 0.596 | 0.12102 | 0.60816 | 2.7644 | L1 | QFD | iDPN N Vigi | 10 | 30 | AC C | 2.7644 | 17.5 | 0.0625 |  |  |  |  | ППГнг(А)-HF | 3 | 2.5 | 5 | 5 | 0.086792 | 1.4586 | 7.41 | 0.116 | 37.05 | 0.58 | Cable tray | [5 empty] | DIFF_2pole | Розетка | Socket |  |  | 6
9 | DB-HD1 | N9 | Convector |  | 0.596 | 9 | 0.98 | 220 | 0.596 | 0.12102 | 0.60816 | 2.7644 | L3 | QFD | iDPN N Vigi | 10 | 30 | AC C | 2.7644 | 17.5 | 0.0625 |  |  |  |  | ППГнг(А)-HF | 3 | 2.5 | 5 | 5 | 0.086792 | 1.4586 | 7.41 | 0.116 | 37.05 | 0.58 | Cable tray | [5 empty] | DIFF_2pole | Розетка | Socket |  |  | 6
10 | DB-HD1 | N10 | Convector |  | 0.596 | 10 | 0.98 | 220 | 0.596 | 0.12102 | 0.60816 | 2.7644 | L2 | QFD | iDPN N Vigi | 10 | 30 | AC C | 2.7644 | 17.5 | 0.0625 |  |  |  |  | ППГнг(А)-HF | 3 | 2.5 | 5 | 5 | 0.086792 | 1.4586 | 7.41 | 0.116 | 37.05 | 0.58 | Cable tray | [5 empty] | DIFF_2pole | Розетка | Socket |  |  | 6
11 | DB-HD1 | N11 | Spare | [10 empty] | QF | iC60N | 16 |  | C | [9 empty] | 2.5 | 5 | 5 | [12 empty] | CB_1pole | Нет | None
12 | DB-HD1 | N12 | Spare | [10 empty] | QF | iC60N | 16 |  | C | [9 empty] | 2.5 | [14 empty] | CB_1pole | Нет | None

## Revit
| Panel name | DB-HD1
№ | Circuit number | Load name | Pi, kW | U, V | CosF | L, m | L (quant.), m
1 | DB-HD1-N1 | Convector | 0.068 | 220 | 0.98 | 20 | 20 | 0.068
2 | DB-HD1-N2 | Convector | 1.008 | 220 | 0.98 | 30 | 35 | 1.008
3 | DB-HD1-N3 | Convector | 0.544 | 220 | 0.98 | 60 | 65 | 0.544
4 | DB-HD1-N4 | Convector | 0.606 | 220 | 0.98 | 5 | 5 | 0.606
5 | DB-HD1-N5 | Convector | 0.596 | 220 | 0.98 | 5 | 5 | 0.596
6 | DB-HD1-N6 | Convector | 0.596 | 220 | 0.98 | 5 | 5 | 0.596
7 | DB-HD1-N7 | Convector | 0.596 | 220 | 0.98 | 5 | 5 | 0.596
8 | DB-HD1-N8 | Convector | 0.596 | 220 | 0.98 | 5 | 5 | 0.596
9 | DB-HD1-N9 | Convector | 0.596 | 220 | 0.98 | 5 | 5 | 0.596
10 | DB-HD1-N10 | Convector | 0.596 | 220 | 0.98 | 5 | 5 | 0.596
11 | DB-HD1-N11 | Convector | 0.596 | 220 | 0.98 | 5 | 5 | 0.596

## Devices
-N0,5
Номинал аппарата |  |  |  | Тип | Кривая | Фазы | Cunsumer | Cunsumer | Да/Нет | BreakerType | IncomerType
0.5 | iC60N | 19 | 20 | QS | B | L1 | None | Нет | Да | CB_1pole | CB_1pole
1 | iC60N |  |  | QF | C | L2 | Socket | Розетка | Нет | CB_3pole | CB_3pole
2 | iC60N |  |  | QFD | D | L3 | Outlet | Вывод |  | DIFF_2pole | SWITCH_1pole
3 | iC60N |  |  |  | AC C | L1,L2,L3 | Circle lighting | Светильник круглый |  | DIFF_4pole | SWITCH_3pole
4 | iC60N | [5 empty] | Linear lighting | Светильник линейный |  | CB_1pole+VDT | CB_1pole+KM
6 | iC60N | [5 empty] | DB | ЩР |  | CB_3pole+VDT | CB_3pole+KM
10 | iC60N | [5 empty] | LDB | ЩО |  | CB_1pole+KM | SWITCH_1pole+KM
13 | iC60N | [5 empty] | CDB | ЩУ |  | CB_3pole+KM | SWITCH_3pole+KM
16 | iC60N | [5 empty] | ELDB | ЩАО |  | DIFF_2pole+KM | CB_1pole+Wh
20 | iC60N | [5 empty] | Lighting transf | ЯТП |  | DIFF_4pole+KM | CB_3pole+Wh
25 | iC60N | [5 empty] | Socket 380V | Розетка 3ф |  | FUSE_1pole | SWITCH_1pole+Wh
32 | iC60N | [5 empty] | Socket IP44 | Розетка IP44 |  | FUSE_2pole | SWITCH_3pole+Wh
40 | iC60N | [5 empty] | Electric Engine | Электродвигатель |  | FUSE_3pole
50 | iC60N | [8 empty] | FUSE_4pole
63 | iC60N | [8 empty] | FUSE_1pole+KM
80 | NSX | [8 empty] | FUSE_2pole+KM
100 | NSX | [8 empty] | FUSE_3pole+KM
125 | NSX | [8 empty] | FUSE_4pole+KM
160 | NSX | [8 empty] | CB_1pole+Wh
CB_3pole+Wh
DIFF_2pole+Wh
DIFF_4pole+Wh

## Cable
Из ГОСТ 50571.5.52-2011
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Таблица С.52.1 - Допустимые токовые нагрузки в амперах для МЕДИ
Способы прокладки по таблице В.52.1 | Число нагруженных проводников и тип изоляции
А1 |  | 3 | 2 |  | 3 | 2
|  | PVC | PVC |  | XLPE | XLPE
А2 | 3 | 2 |  | 3 | 2
| PVC | PVC |  | XLPE | XLPE
В1 |  |  |  | 3 | 2 |  | 3 |  | 2
|  |  |  | PVC | PVC |  | XLPE |  | XLPE
В2 |  |  | 3 | 2 |  | 3 | 2
|  |  | PVC | PVC |  | XLPE | XLPE
С |  |  |  |  | 3 |  | 2 | 3 |  | 2
[5 empty] | PVC |  | PVC | XLPE |  | XLPE
Е | [5 empty] | 3 |  | 2 | 3 |  | 2
[6 empty] | PVC |  | PVC | XLPE |  | XLPE
F | [6 empty] | 3 |  | 2 | 3 |  | 2
[7 empty] | PVC |  | PVC | XLPE |  | XLPE
Саморасчет сечения кабеля по току работает
Допустимые токовые нагрузки, А проводников из меди | [12 empty] | Х | 0.7
1.5 | 13 | 13,5 | 14,5 | 15,5 | 17 | 18.5 | 19,5 | 22 | 23 | 24 | 26 | - |  | 12.95 | 1.5 | 0.2 | 1.5
2.5 | 17,5 | 18 | 19,5 | 21 | 23 | 25 | 27 | 30 | 31 | 33 | 36 | - |  | 17.5 | 2.5
4 | 23 | 24 | 26 | 28 | 31 | 34 | 36 | 40 | 42 | 45 | 49 |  |  | 23.8 | 4
6 | 29 | 31 | 34 | 36 | 40 | 43 | 46 | 51 | 54 | 58 | 63 | - |  | 30.1 | 6
10 | 39 | 42 | 46 | 50 | 54 | 60 | 63 | 70 | 75 | 80 | 66 | - |  | 42 | 10
16 | 52 | 56 | 61 | 68 | 73 | 80 | 85 | 94 | 100 | 107 | 115 | - |  | 56 | 16
25 | 68 | 73 | 80 | 89 | 95 | 101 | 110 | 119 | 127 | 135 | 149 | 161 |  | 70.7 | 25
35 | - | - | - | 110 | 117 | 126 | 137 | 147 | 158 | 169 | 185 | 200 |  | 88.2 | 35
50 | - | - | - | 134 | 141 | 153 | 167 | 179 | 192 | 207 | 225 | 242 |  | 107.1 | 50
70 | - | - | - | 171 | 179 | 196 | 213 | 229 | 246 | 268 | 289 | 310 |  | 137.2 | 70
95 | - | - | - | 207 | 216 | 238 | 258 | 278 | 298 | 328 | 352 | 377 |  | 166.6 | 95
120 | - | - | - | 239 | 249 | 276 | 299 | 322 | 346 | 382 | 410 | 437 |  | 193.2 | 120
150 | - | - | - | - | 285 | 318 | 344 | 371 | 395 | 441 | 473 | 504 |  | 222.6 | 150
185 | - | - | - | - | 324 | 362 | 392 | 424 | 450 | 506 | 542 | 575 |  | 253.4 | 185
240 | - | - | - | - | 380 | 424 | 461 | 500 | 538 | 599 | 641 | 679 |  | 296.8 | 240
[14 empty] | 1000000 | ПЕРЕБОР
Таблица С.52.3 - Поправочные коэффициенты для групп из нескольких контуров или нескольких многожильных кабелей при их совместной прокладке, используются применительно к допустимым токовым нагрузкам по таблице С.52.1
Номер позиции | Устройство электропроводки | Число цепей (контуров) или многожильных кабелей
|  | 1 | 2 | 3 | 4 | 6 | 9 | 12 | 16 | 20
1 | Группами в воздухе, на поверхности, замоноличено или в оболочке | 1,00 | 0,80 | 0,70 | 0,65 | 0,55 | 0,50 | 0,45 | 0,40 | 0,40
2 | Отдельные линии на стенах, полу или на неперфорированных лотках | 1,00 | 0,85 | 0,80 | 0,75 | 0,70 | 0,70 | - | - | -
3 | Отдельные линии, закрепленные непосредственно под деревянным потолком | 0,95 | 0,80 | 0,70 | 0,70 | 0,65 | 0,60 | - | - | -
4 | Отдельные линии на перфорированных горизонтальных или вертикальных лотках | 1,00 | 0,90 | 0,60 | 0,75 | 0,75 | 0,70 | - | - | -
5 | Отдельные линии на лестничных лотках, клицах и т. п. | 1,00 | 0,85 | 0,80 | 0,80 | 0,80 | 0,80 | - | - | -
кабель медь |  |  |  | кабель алюминий
мм^2 | r | x |  | мм^2 | r | x
1.5 | 12.1 | 0.126 |  | 1.5 | 0 | 0
2.5 | 7.41 | 0.116 |  | 2.5 | 0 | 0
4 | 4.61 | 0.107 |  | 4 | 7.74 | 0.107
6 | 3.08 | 0.1 |  | 6 | 5.17 | 0.1
10 | 1.83 | 0.099 |  | 10 | 3.1 | 0.099
16 | 1.15 | 0.095 |  | 16 | 1.94 | 0.095
25 | 0.727 | 0.091 |  | 25 | 1.24 | 0.091
35 | 0.524 | 0.088 |  | 35 | 0.89 | 0.088
50 | 0.387 | 0.085 |  | 50 | 0.62 | 0.085
70 | 0.268 | 0.082 |  | 70 | 0.443 | 0.082
95 | 0.193 | 0.081 |  | 95 | 0.26 | 0.081
120 | 0.153 | 0.08 |  | 120 | 0.258 | 0.08
150 | 0.124 | 0.079 |  | 150 | 0.206 | 0.079
185 | 0.0991 | 0.078 |  | 185 | 0.167 | 0.078
240 | 0.0754 | 0.077 |  | 240 | 0.129 | 0.077
300 | 0.0601 | 0.077

## SC calc
| Transformer |  | Trans to MDB cable | [5 empty] | MDB to SDB cable | [5 empty] | Section of the distribution network No. 2 | [5 empty] | Section of the distribution network No. 3 | [5 empty] | Section of the distribution network No. 4 (DO NOT place data directly)
Transformer type | Rуд.тр.(1) | Xуд.тр.(1) | Lшп. (м) | In ШП / mm^2 | Rуд.шп. | Xуд.шп. | r1шп=r0шп=rнп.шп | x1шп=x0шп=xнп.шп | L (m) | In ШП / mm^2 | Rуд.шп. | Xуд.шп. | r1шп=r0шп=rнп.шп | x1шп=x0шп=xнп.шп | L (m) | mm^2 | Rуд.к. | Xуд.к. | r1к=r0к=rнп.к | x1к=x0к=xнп.к | L (m) | mm^2 | Rуд.к. | Xуд.к. | r1к=r0к=rнп.к | x1к=x0к=xнп.к | Lк. (м) | мм^2 | Rуд.к. | Xуд.к. | r1к=r0к=rнп.к | x1к=x0к=xнп.к
16 | 0.61225 | 4.2885 | 0 | 4250 KBC-II | 0.011 | 0.008 | 0.1508 | 0.154 | 0 | 1600 KBC-II | 0.034 | 0.025 | 18.34 | 3.08 | 0 | 150 | 0.124 | 0.079 | 0 | 0 | 0 | 150 | 0.124 | 0.079 | 0 | 0 | 5 | 4 | 4.61 | 0.107 | 23.05 | 0.535
|  |  | 2 | 240 | 0.0754 | 0.077 |  |  | 35 | 35 | 0.524 | 0.088
r1Σ= | 42.153 | mOm
x1Σ= | 8.0575 | mOm
r0Σ= | 166.7754 | mOm
x0Σ= | 19.3645 | mOm
zкз= | 253.5759 | mOm
√3*Uнн= | 692.8203 | V
Isc(1)= | 2.7322 | kA
zкз= | 42.9162 | mOm
√3*zкз= | 74.3331 | mOm
Uнн= | 400 | V
Isc(3)= | 5.3812 | kA
SHORT CIRCUITS IN ELECTRICAL INSTALLATIONS
CALCULATION METHODS IN ELECTRICAL
INSTALLATIONS AC VOLTAGE
UP TO 1 kVGOST 28249-93
Short current L-N Isc(1).
Short current L-L Isc(3).
SHORT CIRCUITS IN ELECTRICAL INSTALLATIONS
CALCULATION METHODS IN ELECTRICAL
INSTALLATIONS AC VOLTAGE
UP TO 1 kVGOST 28249-93
Short current L-N Isc(1).
𝐼_кз^((1) )=(√3×𝑈_нн)/(𝑍_кз^((1) ) );
𝑍_кз^((1))=√((2×𝑥_1+𝑥_0 )^2+〖(2×𝑟_1+𝑟_0)〗^(2 ) )
Short current L-L Isc(3).
𝐼_кз^((3) )=𝑈_нн/(〖√3×𝑍〗_кз^((3) ) );
𝑍_кз^((3))=√(𝑥_1^2+𝑟_1^2 )

## tab_r_x
| Cable |  |  |  |  | Busbars EAE
| мм^2 | r | x |  |  | In, A | r_(t окр. среды 35град цельсия) | x | [6 empty] | № | Tr-r | S tr | I | U кз | Z тр | P кз | R тр | X тр
| 1.5 | 12.1 | 0.126 |  | Магистральные шинопроводы | 1000 KBC-II | 0.052 | 0.03 | [7 empty] | type | kVA | kA | % | mOm | kW | mOm | mOm
| 2.5 | 7.41 | 0.116 |  |  | 1250 KBC-II | 0.048 | 0.032 | [6 empty] | 1 | TM - | 250 | 0.38029 | 4.5 | 25.992 | 3.7 | 8.5282 | 24.5531
| 4 | 4.61 | 0.107 |  |  | 1600 KBC-II | 0.034 | 0.025 | [6 empty] | 2 | TM - | 400 | 0.60846 | 4.5 | 16.245 | 5.5 | 4.952 | 15.4718
| 6 | 3.08 | 0.1 |  |  | 2000 KBC-II | 0.026 | 0.02 | [6 empty] | 3 | TM - | 630 | 0.95832 | 4.5 | 10.3143 | 7.6 | 2.7585 | 9.9386
| 10 | 1.83 | 0.099 |  |  | 2250 KBC-II | 0.02 | 0.016 | [6 empty] | 4 | TM - | 1000 | 1.5211 | 5.5 | 7.942 | 12.2 | 1.7575 | 7.7451
| 16 | 1.15 | 0.095 |  |  | 2500 KBC-II | 0.024 | 0.016 | [6 empty] | 5 | TM - | 1250 | 1.9014 | 5.5 | 6.3536 | 13.5 | 1.2447 | 6.2305
| 25 | 0.727 | 0.091 |  |  | 3000 KBC-II | 0.018 | 0.012 | [6 empty] | 6 | TM - | 1600 | 2.4338 | 5.5 | 4.9637 | 18 | 1.0129 | 4.8593
| 35 | 0.524 | 0.088 |  |  | 3600 KBC-II | 0.013 | 0.01 | [6 empty] | 7 | TM - | 2500 | 3.8029 | 5.5 | 3.1768 | 26 | 0.59928 | 3.1198
| 50 | 0.387 | 0.085 |  |  | 4250 KBC-II | 0.011 | 0.008 | [6 empty] | 8 | TM - | 4000 | 6.0846 | 6.5 | 2.3465 | 33.5 | 0.30162 | 2.327
| 70 | 0.268 | 0.082 |  |  | 4400 KBC-II | 0.012 | 0.008 | [6 empty] | 9 | TM - | 6300 | 9.5832 | 6.5 | 1.4898 | 46.5 | 0.16878 | 1.4803
| 95 | 0.193 | 0.081 |  |  | 5300 KBC-II | 0.009 | 0.006
| 120 | 0.153 | 0.08 |  |  | 6300 KBC-II | 0.007 | 0.005 | [6 empty] | 10 | Trihal | 500 | 0.76057 | 4 | 11.552 | 6 | 3.4574 | 11.0225
| 150 | 0.124 | 0.079 |  |  | 0800 KBA | 0.07 | 0.032 | [6 empty] | 11 | Trihal | 630 | 0.95832 | 4 | 9.1683 | 7.3 | 2.6496 | 8.777
| 185 | 0.0991 | 0.078 |  |  | 1000 KBA | 0.051 | 0.025 | [6 empty] | 12 | Trihal | 800 | 1.2169 | 6 | 10.83 | 8.8 | 1.9808 | 10.6473
| 240 | 0.0754 | 0.077 |  |  | 1250 KBA | 0.04 | 0.019 | [6 empty] | 13 | Trihal | 1000 | 1.5211 | 6 | 8.664 | 10 | 1.4406 | 8.5434
| 300 | 0.0601 | 0.077 |  |  | 1600 KBA | 0.034 | 0.017 | [6 empty] | 14 | Trihal | 1250 | 1.9014 | 6 | 6.9312 | 12 | 1.1064 | 6.8423
| 1,5 Al | 18.1 | 0.126 |  |  | 1600/2 KBA | 0.036 | 0.016 | [6 empty] | 15 | Trihal | 1600 | 2.4338 | 6 | 5.415 | 14 | 0.78782 | 5.3574
| 2,5 Al | 12.1 | 0.116 |  |  | 2000 KBA | 0.025 | 0.013 | [6 empty] | 16 | Trihal | 2000 | 3.0423 | 6 | 4.332 | 17 | 0.61225 | 4.2885
| 4 Al | 7.41 | 0.107 |  |  | 2500 KBA | 0.02 | 0.01 | [6 empty] | 17 | Trihal | 2500 | 3.8029 | 6 | 3.4656 | 21 | 0.48404 | 3.4316
| 6 Al | 5.11 | 0.1 |  |  | 3100 KBA | 0.017 | 0.009 | [6 empty] | 18 | Trihal | 3150 | 4.7916 | 7 | 3.2089 | 25 | 0.36296 | 3.1883
| 10 Al | 3.08 | 0.099 |  |  | 3200 KBA | 0.017 | 0.008
| 16 Al | 1.91 | 0.095 |  |  | 4000 KBA | 0.013 | 0.007 | [6 empty] | 19 | Newton | 1250 | 1.9014 | 5 | 5.776 | 12 | 1.1064 | 5.669
| 25 Al | 1.2 | 0.091 |  |  | 4250 KBA | 0.011 | 0.005
| 35 Al | 0.868 | 0.088 |  |  | 5000 KBA | 0.01 | 0.005
| 50 Al | 0.641 | 0.085 |  | Распределительные шинопроводы | 160 KOA | 0.286 | 0.205
| 70 Al | 0.443 | 0.082 |  |  | 250 KOA | 0.246 | 0.183
| 95 Al | 0.32 | 0.081 |  |  | 315 KOA | 0.204 | 0.165
| 120 Al | 0.253 | 0.08 |  |  | 400 KOA | 0.125 | 0.118
| 150 Al | 0.206 | 0.079 |  |  | 500 KOA | 0.109 | 0.103
| 185 Al | 0.164 | 0.078 |  |  | 600 KOA | 0.094 | 0.088
| 240 Al | 0.125 | 0.077 |  |  | 250 KOC | 0.18 | 0.173
| 300 Al | 0.1 | 0.077 |  |  | 315 KOC | 0.164 | 0.154
[6 empty] | 400 KOC | 0.144 | 0.144
[6 empty] | 600 KOC | 0.078 | 0.117
[6 empty] | 800 KOC | 0.068 | 0.083
Интерполяция (коэффициенты одновременности для квартир повышенной комфортности)
6 | 0 | 9 | 0 | 12 | 0 | 15 | 0 | 18 | 0 | 24 | 0 | 40 | 0 | 60 | 0 | 100 | 184 | 200 | 0 | 400 | 0 | 600
0.51 | 0.77 | 0.38 | 0.56 | 0.32 | 0.44 | 0.29 | 0.44 | 0.26 | 0.32 | 0.24 | 0.3 | 0.2 | 0.24 | 0.18 | 0.21 | 0.16 | 0.1432 | 0.14 | 0.15 | 0.13 | 0.17 | 0.11